{"text_format":"2","workbook":"xls","n_sheets":1,"sheets":["Products"],"not_rendered":{"charts":0,"images":0,"macros":0,"external_links":1,"defined_names":0,"comments":0,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"run_cost":"one","rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900","formulas":"cached_only"}

{"sheet":"Products","index":0,"n_rows":33,"n_cols":8,"rows_kept":33,"cut":false,"hidden":false,"merged":[],"flags":["formulas_cached_only"]}
["PRODUCT NAME","ARXM-M"]
[]
[]
[]
[]
["","","","","","ARXM50MV1B","ARXM25M2V1B (Archived)","ARXM35M2V1B (Archived)"]
["Mõõtmed","Ühik","","Kõrgus","mm","735","550","550"]
["","","","Laius","mm","825","765","765"]
["","","","Sügavus","mm","300","285","285"]
["Kaal","Ühik","","","kg","44","32","32"]
["Kompressor","Tüüp","","","","Hermeetiline pöördkompressor","Hermeetiline pöördkompressor","Hermeetiline pöördkompressor"]
["Töövahemik","Jahutus","Keskkond","Min","° CDB","-10","-10","-10"]
["","","","Max","° CDB","46","46","46"]
["","Küte","Keskkond","Min","°CWB","-15","-15","-15"]
["","","","Max","°CWB","18","18","18"]
["Mürarõhutase","Jahutus","","kiire","dBA","48","46","49"]
["","","","aeglane","dBA","44"]
["","Küte","","kiire","dBA","49","47","49"]
["","","","aeglane","dBA","45"]
["Külmaaine","Tüüp","","","","R-32","R-32","R-32"]
["","Kogus","","","kg","1.4","0.76","0.76"]
["","Kogus","","","tCO2Eq","0.9","0.5","0.5"]
["","GWP","","","","675","675","675"]
["Torustikuühendused","Torustiku pikkus","Max","OU - IU","m","30","15","15"]
["","Jahutusaine lisatäide","","","kg/m","0,02 (torustikule, mille pikkus ületab 10 m)","0,02 (torustikule, mille pikkus ületab 10 m)","0,02 (torustikule, mille pikkus ületab 10 m)"]
["","Kõrguste vahe","IU - OU","Max","m","20","12","12"]
["Standardsed lisatarvikud","Installation manual","","","","1","1","1"]
["","Refrigerant charge label","","","","1","1","1"]
["","Multilingual fluorinated greenhouse gases labels","","","","1","1","1"]
["","Drain plug (only heat pump models)","","","","1","1","1"]
["Elektritoide","Faas","","","","1~","1~","1~"]
["","Sagedus","","","Hz","50","50","50"]
["","Pinge","","","V","220-240","220-240","220-240"]