{"text_format":"2","workbook":"xls","n_sheets":1,"sheets":["Products"],"not_rendered":{"charts":0,"images":0,"macros":0,"external_links":1,"defined_names":0,"comments":0,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"run_cost":"one","rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900","formulas":"cached_only"}

{"sheet":"Products","index":0,"n_rows":44,"n_cols":11,"rows_kept":44,"cut":false,"hidden":false,"merged":[],"flags":["formulas_cached_only"]}
["PRODUCT NAME","EWAA-DV3P-H"]
[]
[]
[]
[]
["","","","","","EWAA004D2V3P-H","EWAA006D2V3P-H","EWAA008D2V3P-H","EWAA011DAV3P-H-","EWAA014DAV3P-H-","EWAA016DAV3P-H-"]
["Jahutusvõimsus","Nom","","","kW","4.86 (1), 4.52 (2)","5.83 (1), 5.09 (2)","6.18 (1), 5.44 (2)","11.6 (1), 11.5 (2)","12.8 (1), 12.7 (2)","14.0 (1), 15.3 (2)"]
["Võimsuse juhtimine","Meetod","","","","Muutuv (inverter)","Muutuv (inverter)","Muutuv (inverter)","Muutuv (inverter)","Muutuv (inverter)","Muutuv (inverter)"]
["Sisendvõimsus","Jahutus","","Nom","kW","0.820 (1), 1.36 (2)","1.08 (1), 1.55 (2)","1.19 (1), 1.73 (2)","3.56 (1), 2.17 (2)","4.06 (1), 2.51 (2)","4.58 (1), 3.24 (2)"]
["EER","","","","","5.91 (1), 3.32 (2)","5.40 (1), 3.28 (2)","5.19 (1), 3.14 (2)","3.26 (1), 5.31 (2)","3.16 (1), 5.04 (2)","3.06 (1), 4.74 (2)"]
["SEER","","","","","","","","5.79 (5)","5.71 (5)","5.59 (5)"]
["Mõõtmed","Ühik","","Sügavus","mm","362","362","362","460","460","460"]
["","","","Kõrgus","mm","770","770","770","870","870","870"]
["","","","Laius","mm","1250","1250","1250","1380","1380","1380"]
["Kaal","Ühik","","","kg","88","88","88","147","147","147"]
["Korpus","Värvus","","","","Elevandiluuvalge","Elevandiluuvalge","Elevandiluuvalge","Elevandiluuvalge","Elevandiluuvalge","Elevandiluuvalge"]
["","Materjal","","","","Tsingitud madalsüsinikteras","Tsingitud madalsüsinikteras","Tsingitud madalsüsinikteras","Polüestervärviga kaetud galvaanitud terasplaat","Polüestervärviga kaetud galvaanitud terasplaat","Polüestervärviga kaetud galvaanitud terasplaat"]
["Õhu soojusvaheti","Tüüp","","","","","","","Väga tõhus ribi ja toru tüüp integreeritud järeljahutiga","Väga tõhus ribi ja toru tüüp integreeritud järeljahutiga","Väga tõhus ribi ja toru tüüp integreeritud järeljahutiga"]
["Ventilaator","Kogus","","","","1","1","1","1","1","1"]
["","Tüüp","","","","Tiivikventilaator","Tiivikventilaator","Tiivikventilaator","Tiivikventilaator","Tiivikventilaator","Tiivikventilaator"]
["Ventilaatori mootor","Ajam","","","","","","","Otseühendus","Otseühendus","Otseühendus"]
["Kompressor","Kogus_","","","","1","1","1","1","1","1"]
["Kompressor","Tüüp","","","","Hermeetiline pöördkompressor","Hermeetiline pöördkompressor","Hermeetiline pöördkompressor","Hermeetiliselt suletud inverteriga pöördkompressor","Hermeetiliselt suletud inverteriga pöördkompressor","Hermeetiliselt suletud inverteriga pöördkompressor"]
["Kompressor","Käivitusmeetod_","","","","","","","Inverterjuhtimisega","Inverterjuhtimisega","Inverterjuhtimisega"]
["Töövahemik","Õhu pool","Jahutus","Min","° CDB","10 (3)","10 (3)","10 (3)","10","10","10"]
["","","","Max","° CDB","43","43","43","43","43","43"]
["Töötamisvahemik","Veepool","Aurusti","Min.","° CDB","5 (3)","5 (3)","5 (3)","5","5","5"]
["","","","Max","° CDB","22","22","22","22","22","22"]
["Müratase","Jahutus","","Nom","dBA","61","62","62","67.0","69.0","69.0"]
["Mürarõhutase","Jahutus","","Nom","dBA","48","49","50","47.7","50.8","51.0"]
["Külmaaine","Tüüp","","","","R-32","R-32","R-32","R-32","R-32","R-32"]
["","GWP","","","","675","675","675","675.0","675.0","675.0"]
["","Kogus","","","kg","1.35","1.35","1.35"]
["Jahutusaine","Ahelad","","Kogus","","","","","1","1","1"]
["Elektritoide","Faas","","","","1~","1~","1~","1~","1~","1~"]
["","Sagedus","","","Hz","50","50","50","50","50","50"]
["","Pinge","","","V","230 +/-10%","230 +/-10%","230 +/-10%","230","230","230"]
["","Pingevahemik","","Min","%","","","","-10","-10","-10"]
["","","","Max","%","","","","10","10","10"]
["Ühik","Töövool","","Max","A","","","","30.8","30.8","30.8"]
["Märkused","","","","","(1) - Tingimus 1: jahutus Ta 35 °C - LWE 18°C (DT = 5°C); kütmine Ta DB/WB 7 °C / 6 °C - LWC 35 °C (DT = 5 °C)","(1) - Tingimus 1: jahutus Ta 35 °C - LWE 18°C (DT = 5°C); kütmine Ta DB/WB 7 °C / 6 °C - LWC 35 °C (DT = 5 °C)","(1) - Tingimus 1: jahutus Ta 35 °C - LWE 18°C (DT = 5°C); kütmine Ta DB/WB 7 °C / 6 °C - LWC 35 °C (DT = 5 °C)","(1) - Jahutus: EW 12 ℃; LW 7 ℃; ümbritseva keskkonna tingimused: 35 °C DB","(1) - Jahutus: EW 12 ℃; LW 7 ℃; ümbritseva keskkonna tingimused: 35 °C DB","(1) - Jahutus: EW 12 ℃; LW 7 ℃; ümbritseva keskkonna tingimused: 35 °C DB"]
["","","","","","(2) - Tingimus 2: jahutus Ta 35 °C - LWE 7°C (DT = 5°C); kütmine Ta DB/WB 7 °C / 6 °C - LWC 45°C (DT = 5 °C)","(2) - Tingimus 2: jahutus Ta 35 °C - LWE 7°C (DT = 5°C); kütmine Ta DB/WB 7 °C / 6 °C - LWC 45°C (DT = 5 °C)","(2) - Tingimus 2: jahutus Ta 35 °C - LWE 7°C (DT = 5°C); kütmine Ta DB/WB 7 °C / 6 °C - LWC 45°C (DT = 5 °C)","(2) - Jahutus: EW 23 ℃; LW 18 ℃; ümbritseva keskkonna tingimused: 35 °C DB","(2) - Jahutus: EW 23 ℃; LW 18 ℃; ümbritseva keskkonna tingimused: 35 °C DB","(2) - Jahutus: EW 23 ℃; LW 18 ℃; ümbritseva keskkonna tingimused: 35 °C DB"]
["","","","","","(3) - Enama teabe sammiseks vt talitlusvahemiku joonist","(3) - Enama teabe sammiseks vt talitlusvahemiku joonist","(3) - Enama teabe sammiseks vt talitlusvahemiku joonist","(3) - Vastavalt standardile EN14825","(3) - Vastavalt standardile EN14825","(3) - Vastavalt standardile EN14825"]
["","","","","","","","","(4) - Olenevalt töörežiimist, vt paigaldusjuhendit.","(4) - Olenevalt töörežiimist, vt paigaldusjuhendit.","(4) - Olenevalt töörežiimist, vt paigaldusjuhendit."]