{"text_format":"2","workbook":"xls","n_sheets":1,"sheets":["Products"],"not_rendered":{"charts":0,"images":0,"macros":0,"external_links":1,"defined_names":0,"comments":0,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"run_cost":"one","rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900","formulas":"cached_only"}

{"sheet":"Products","index":0,"n_rows":48,"n_cols":8,"rows_kept":48,"cut":false,"hidden":false,"merged":[],"flags":["formulas_cached_only"]}
["PRODUCT NAME","EWAA-DW1P-H"]
[]
[]
[]
[]
["","","","","","EWAA011DAW1P-H-","EWAA014DAW1P-H-","EWAA016DAW1P-H-"]
["Mürarõhutase","Jahutus","","Nom","dBA","47.7","50.8","51.0"]
["Hüdraulilised komponendid","Paisupaak","","Maht","l","8","8","8"]
["Töövahemik","Õhu pool","Jahutus","Min","° CDB","10","10","10"]
["","","","Max","° CDB","43","43","43"]
["","Veepool","Jahutus","Max","° CDB","22","22","22"]
["","","","Min","° CDB","5","5","5"]
["Jahutusaine kogus","Kontuuri kohta","","","kg","3.80","3.80","3.80"]
["","Refrigerant charge-=-Per circuit-=-TCO2Eq","","","TCO2Eq","2.6","2.6","2.6"]
["Kompressor","Tüüp","","","","Hermeetiliselt suletud inverteriga pöördkompressor","Hermeetiliselt suletud inverteriga pöördkompressor","Hermeetiliselt suletud inverteriga pöördkompressor"]
["","Käivitusmeetod_","","","","Inverterjuhtimisega","Inverterjuhtimisega","Inverterjuhtimisega"]
["","Kogus_","","","","1","1","1"]
["Õhu soojusvaheti","Tüüp","","","","Väga tõhus ribi ja toru tüüp integreeritud järeljahutiga","Väga tõhus ribi ja toru tüüp integreeritud järeljahutiga","Väga tõhus ribi ja toru tüüp integreeritud järeljahutiga"]
["Kaal","Ühik","","","kg","147","147","147"]
["EER","","","","","3.26 (1), 5.31 (2)","3.16 (1), 5.04 (2)","3.06 (1), 4.74 (2)"]
["Külmaaine","GWP","","","","675.0","675.0","675.0"]
["","Tüüp","","","","R-32","R-32","R-32"]
["","Ahelad","","Kogus","","1","1","1"]
["","Juhtimine","","","","Elektrooniline paisuventiil","Elektrooniline paisuventiil","Elektrooniline paisuventiil"]
["Ventilaatori mootor","Kiirus","Jahutus","Nom","p/min","550","650","650"]
["Jahutusvõimsus","Nom","","","kW","11.6 (1), 11.5 (2)","12.8 (1), 12.7 (2)","14.0 (1), 15.3 (2)"]
["Vee soojusvaheti","Vee maht","","","l","2","2","2"]
["","Minimaalne veehulk süsteemis","","","l","20 (6)","20 (6)","20 (6)"]
["","Tüüp","","","","Plaatsoojusvaheti","Plaatsoojusvaheti","Plaatsoojusvaheti"]
["Power input","Jahutus","","Nom","kW","3.56 (1), 2.17 (2)","4.06 (1), 2.51 (2)","4.58 (1), 3.24 (2)"]
["Sound power level","Jahutus","","Nom","dBA","67.0","69.0","69.0"]
["Mõõtmed","Ühik","","Laius","mm","1,380","1,380","1,380"]
["","","","Sügavus","mm","460","460","460"]
["","","","Kõrgus","mm","870","870","870"]
["Võimsuskontroll","Meetod","","","","Muutuv (inverter)","Muutuv (inverter)","Muutuv (inverter)"]
["Ventilaator","Õhu vooluhulk","Jahutus","Nom","m³/min","70","85","85"]
["Kompressor","Käivitusmeetod_","","","","Inverter","Inverter","Inverter"]
["Power supply","Faas","","","","3~","3~","3~"]
["","Sagedus","","","Hz","50","50","50"]
["","Nimetus","","","","W1","W1","W1"]
["","Pinge","","","V","400","400","400"]
["Märkused","","","","","(1) - Jahutus: EW 12 ℃; LW 7 ℃; ümbritseva keskkonna tingimused: 35 °C DB","(1) - Jahutus: EW 12 ℃; LW 7 ℃; ümbritseva keskkonna tingimused: 35 °C DB","(1) - Jahutus: EW 12 ℃; LW 7 ℃; ümbritseva keskkonna tingimused: 35 °C DB"]
["","","","","","(2) - Jahutus: EW 23 ℃; LW 18 ℃; ümbritseva keskkonna tingimused: 35 °C DB","(2) - Jahutus: EW 23 ℃; LW 18 ℃; ümbritseva keskkonna tingimused: 35 °C DB","(2) - Jahutus: EW 23 ℃; LW 18 ℃; ümbritseva keskkonna tingimused: 35 °C DB"]
["","","","","","(3) - Tingimus: Ta DB/WB 7 °C / 6 °C - LWC 35 °C (DT = 5 °C)","(3) - Tingimus: Ta DB/WB 7 °C / 6 °C - LWC 35 °C (DT = 5 °C)","(3) - Tingimus: Ta DB/WB 7 °C / 6 °C - LWC 35 °C (DT = 5 °C)"]
["","","","","","(4) - Tingimus: Ta DB/WB 7 °C/6 °C - LWC 45 °C (Dt=5 °C)","(4) - Tingimus: Ta DB/WB 7 °C/6 °C - LWC 45 °C (Dt=5 °C)","(4) - Tingimus: Ta DB/WB 7 °C/6 °C - LWC 45 °C (Dt=5 °C)"]
["","","","","","(5) - Vastavalt standardile EN14825","(5) - Vastavalt standardile EN14825","(5) - Vastavalt standardile EN14825"]
["","","","","","(6) - Olenevalt töörežiimist, vt paigaldusjuhendit.","(6) - Olenevalt töörežiimist, vt paigaldusjuhendit.","(6) - Olenevalt töörežiimist, vt paigaldusjuhendit."]
["","","","","","(7) - Enama teabe sammiseks vt talitlusvahemiku joonist","(7) - Enama teabe sammiseks vt talitlusvahemiku joonist","(7) - Enama teabe sammiseks vt talitlusvahemiku joonist"]