{"text_format":"2","workbook":"xls","n_sheets":1,"sheets":["Products"],"not_rendered":{"charts":0,"images":0,"macros":0,"external_links":1,"defined_names":0,"comments":0,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"run_cost":"one","rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900","formulas":"cached_only"}

{"sheet":"Products","index":0,"n_rows":51,"n_cols":12,"rows_kept":51,"cut":false,"hidden":false,"merged":[],"flags":["formulas_cached_only"]}
["PRODUCT NAME","EWWH-J-SS"]
[]
[]
[]
[]
["","","","","","EWWH090J-SS","EWWH110J-SS","EWWH120J-SS","EWWH130J-SS","EWWH150J-SS","EWWH180J-SS","EWWH200J-SS"]
["Mürarõhutase","Jahutus","","Nom","dBA","79","79","79","79","79","79","79"]
["Töövahemik","Veepool","Aurusti","Min.","° CDB","-5","-5","-5","-5","-5","-5","-5"]
["","","","Max","° CDB","25","25","25","25","25","25","25"]
["Kompressor","Tüüp","","","","Üheastmeline kruvikompressor","Üheastmeline kruvikompressor","Üheastmeline kruvikompressor","Üheastmeline kruvikompressor","Üheastmeline kruvikompressor","Üheastmeline kruvikompressor","Üheastmeline kruvikompressor"]
["","Käivitusmeetod_","","","","Wye-Delta","Wye-Delta","Wye-Delta","Wye-Delta","Wye-Delta","Wye-Delta","Wye-Delta"]
["","Kogus_","","","","1","1","1","1","1","1","1"]
["Kaal","Töökaal","","","kg","1,211","1,276","1,378","1,415","1,473","1,663","1,607"]
["","Ühik","","","kg","1,177","1,233","1,334","1,366","1,416","1,600","1,675"]
["EER","","","","","3.85","3.75","3.72","3.78","3.82","3.67","3.66"]
["Külmaaine","Tüüp","","","","R-1234(ze)","R-1234(ze)","R-1234(ze)","R-1234(ze)","R-1234(ze)","R-1234(ze)","R-1234(ze)"]
["","GWP","","","","7","7","7","7","7","7","7"]
["","Ahelad","","Kogus","","1","1","1","1","1","1","1"]
["","Charge","","","kg","18","35","34","37","37","38","38"]
["Jahutusvõimsus","Nom","","","kW","88.77","107.1","115.1","133.5","150.1","181.6","200.6"]
["IPLV","","","","","4.1","4.11","4.09","4.11","4.12","4.64","4.6"]
["Toruühendused","Aurusti vee sisselase/väljalase (OD)","","","","76.2 mm","76.2 mm","76.2 mm","76.2 mm","76.2 mm","76.2 mm","76.2 mm"]
["SEER","","","","","3.36","3.38","3.32","3.4","3.39","3.87","3.82"]
["Power input","Jahutus","","Nom","kW","30","36.3","41.7","47.8","54.2","65.7","74.4"]
["Sound power level","Jahutus","","Nom","dBA","89","89","89","89","89","89","89"]
["Mõõtmed","Ühik","","Laius","mm","913","913","913","913","913","913","913"]
["","","","Sügavus","mm","2,684","2,684","2,684","2,684","2,684","2,684","2,684"]
["","","","Kõrgus","mm","1,020","1,020","1,020","1,020","1,020","1,020","1,020"]
["Võimsuskontroll","Minimaalne maht","","","%","25","25","25","25","25","25","25"]
["","Meetod","","","","Astmeteta","Astmeteta","Astmeteta","Astmeteta","Astmeteta","Astmeteta","Astmeteta"]
["Korpus","Materjal","","","","Galvaanitud teras","Galvaanitud teras","Galvaanitud teras","Galvaanitud teras","Galvaanitud teras","Galvaanitud teras","Galvaanitud teras"]
["","Värvus","","","","Elevandiluuvalge","Elevandiluuvalge","Elevandiluuvalge","Elevandiluuvalge","Elevandiluuvalge","Elevandiluuvalge","Elevandiluuvalge"]
["Vee soojusvaheti - aurusti","Tüüp","","","","Plaatsoojusvaheti.","Plaatsoojusvaheti.","Plaatsoojusvaheti.","Plaatsoojusvaheti.","Plaatsoojusvaheti.","Plaatsoojusvaheti.","Plaatsoojusvaheti."]
["","Vee rõhulangus","Jahutus","Nom","kPa","10.7","10.9","19.3","19.3","17.8","16.8","20.1"]
["","Vee maht","","","l","14","18","14","17","20","26","26"]
["Power supply","Faas","","","","3~","3~","3~","3~","3~","3~","3~"]
["","Pingevahemik","","Max","%","10","10","10","10","10","10","10"]
["","","","Min","%","-10","-10","-10","-10","-10","-10","-10"]
["","Sagedus","","","Hz","50","50","50","50","50","50","50"]
["","Pinge","","","V","400","400","400","400","400","400","400"]
["Seade","Maksimaalne seadme vool juhtmestiku dimensioonimiseks","","","A","83","100","112","127","159","176","198"]
["","Käivitusvool","","Max","A","153","153","197","197","197","290","290"]
["","Töövool","Jahutus","Nom","A","39","44","55","60","65","76","84"]
["","","","Max","A","75","90","100","114","143","158","178"]
["Märkused","","","","","(1) - Jahutus: EW 12 ℃; LW 7 ℃; ümbritseva keskkonna tingimused: 35 °C DB","(1) - Jahutus: EW 12 ℃; LW 7 ℃; ümbritseva keskkonna tingimused: 35 °C DB","(1) - Jahutus: EW 12 ℃; LW 7 ℃; ümbritseva keskkonna tingimused: 35 °C DB","(1) - Jahutus: EW 12 ℃; LW 7 ℃; ümbritseva keskkonna tingimused: 35 °C DB","(1) - Jahutus: EW 12 ℃; LW 7 ℃; ümbritseva keskkonna tingimused: 35 °C DB","(1) - Jahutus: EW 12 ℃; LW 7 ℃; ümbritseva keskkonna tingimused: 35 °C DB","(1) - Jahutus: EW 12 ℃; LW 7 ℃; ümbritseva keskkonna tingimused: 35 °C DB"]
["","","","","","(2) - Jahutus: EW 23 ℃; LW 18 ℃; ümbritseva keskkonna tingimused: 35 °C DB","(2) - Jahutus: EW 23 ℃; LW 18 ℃; ümbritseva keskkonna tingimused: 35 °C DB","(2) - Jahutus: EW 23 ℃; LW 18 ℃; ümbritseva keskkonna tingimused: 35 °C DB","(2) - Jahutus: EW 23 ℃; LW 18 ℃; ümbritseva keskkonna tingimused: 35 °C DB","(2) - Jahutus: EW 23 ℃; LW 18 ℃; ümbritseva keskkonna tingimused: 35 °C DB","(2) - Jahutus: EW 23 ℃; LW 18 ℃; ümbritseva keskkonna tingimused: 35 °C DB","(2) - Jahutus: EW 23 ℃; LW 18 ℃; ümbritseva keskkonna tingimused: 35 °C DB"]
["","","","","","(3) - Tingimus: Ta DB/WB 7 °C / 6 °C - LWC 35 °C (DT = 5 °C)","(3) - Tingimus: Ta DB/WB 7 °C / 6 °C - LWC 35 °C (DT = 5 °C)","(3) - Tingimus: Ta DB/WB 7 °C / 6 °C - LWC 35 °C (DT = 5 °C)","(3) - Tingimus: Ta DB/WB 7 °C / 6 °C - LWC 35 °C (DT = 5 °C)","(3) - Tingimus: Ta DB/WB 7 °C / 6 °C - LWC 35 °C (DT = 5 °C)","(3) - Tingimus: Ta DB/WB 7 °C / 6 °C - LWC 35 °C (DT = 5 °C)","(3) - Tingimus: Ta DB/WB 7 °C / 6 °C - LWC 35 °C (DT = 5 °C)"]
["","","","","","(4) - Tingimus: Ta DB/WB 7 °C/6 °C - LWC 45 °C (Dt=5 °C)","(4) - Tingimus: Ta DB/WB 7 °C/6 °C - LWC 45 °C (Dt=5 °C)","(4) - Tingimus: Ta DB/WB 7 °C/6 °C - LWC 45 °C (Dt=5 °C)","(4) - Tingimus: Ta DB/WB 7 °C/6 °C - LWC 45 °C (Dt=5 °C)","(4) - Tingimus: Ta DB/WB 7 °C/6 °C - LWC 45 °C (Dt=5 °C)","(4) - Tingimus: Ta DB/WB 7 °C/6 °C - LWC 45 °C (Dt=5 °C)","(4) - Tingimus: Ta DB/WB 7 °C/6 °C - LWC 45 °C (Dt=5 °C)"]
["","","","","","(5) - Vastavalt standardile EN14825","(5) - Vastavalt standardile EN14825","(5) - Vastavalt standardile EN14825","(5) - Vastavalt standardile EN14825","(5) - Vastavalt standardile EN14825","(5) - Vastavalt standardile EN14825","(5) - Vastavalt standardile EN14825"]
["","","","","","(6) - Olenevalt töörežiimist, vt paigaldusjuhendit.","(6) - Olenevalt töörežiimist, vt paigaldusjuhendit.","(6) - Olenevalt töörežiimist, vt paigaldusjuhendit.","(6) - Olenevalt töörežiimist, vt paigaldusjuhendit.","(6) - Olenevalt töörežiimist, vt paigaldusjuhendit.","(6) - Olenevalt töörežiimist, vt paigaldusjuhendit.","(6) - Olenevalt töörežiimist, vt paigaldusjuhendit."]
["","","","","","(7) - Enama teabe sammiseks vt talitlusvahemiku joonist","(7) - Enama teabe sammiseks vt talitlusvahemiku joonist","(7) - Enama teabe sammiseks vt talitlusvahemiku joonist","(7) - Enama teabe sammiseks vt talitlusvahemiku joonist","(7) - Enama teabe sammiseks vt talitlusvahemiku joonist","(7) - Enama teabe sammiseks vt talitlusvahemiku joonist","(7) - Enama teabe sammiseks vt talitlusvahemiku joonist"]