{"text_format":"2","workbook":"xls","n_sheets":1,"sheets":["Products"],"not_rendered":{"charts":0,"images":0,"macros":0,"external_links":1,"defined_names":0,"comments":0,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"run_cost":"one","rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900","formulas":"cached_only"}

{"sheet":"Products","index":0,"n_rows":20,"n_cols":9,"rows_kept":20,"cut":false,"hidden":false,"merged":[],"flags":["formulas_cached_only"]}
["PRODUCT NAME","VH-B"]
[]
[]
[]
[]
["","","","VH1B","VH2B","VH3B","VH4/AB","VH4B","VH5B"]
["Väljundvool (maksimaalne)","","","19 A temeratuuril 40 °C (ümbritsev)","19 A temeratuuril 40 °C (ümbritsev)","19 A temeratuuril 40 °C (ümbritsev)","19 A temeratuuril 40 °C (ümbritsev)","19 A temeratuuril 40 °C (ümbritsev)","19 A temeratuuril 40 °C (ümbritsev)"]
["Ühendatav seade","","","VAM150FA","VAM250FA, VAM350FB","VAM500FB, VAM650FB","VAM800FB, VAM1000FB","VAM800FB, VAM1000FB","VAM1500FB, VAM2000FB"]
["LED-indikaatorid","","","Toide SEES – kollane, Kütteseade SEES – punane (püsiv või vilkuv, osutades impulssjuhtimisele), Õhuvoolu tõrge – punane","Toide SEES – kollane, Kütteseade SEES – punane (püsiv või vilkuv, osutades impulssjuhtimisele), Õhuvoolu tõrge – punane","Toide SEES – kollane, Kütteseade SEES – punane (püsiv või vilkuv, osutades impulssjuhtimisele), Õhuvoolu tõrge – punane","Toide SEES – kollane, Kütteseade SEES – punane (püsiv või vilkuv, osutades impulssjuhtimisele), Õhuvoolu tõrge – punane","Toide SEES – kollane, Kütteseade SEES – punane (püsiv või vilkuv, osutades impulssjuhtimisele), Õhuvoolu tõrge – punane","Toide SEES – kollane, Kütteseade SEES – punane (püsiv või vilkuv, osutades impulssjuhtimisele), Õhuvoolu tõrge – punane"]
["Käitamisrelee","","","1 A 120 V AC või 1 A 24 V DC","1 A 120 V AC või 1 A 24 V DC","1 A 120 V AC või 1 A 24 V DC","1 A 120 V AC või 1 A 24 V DC","1 A 120 V AC või 1 A 24 V DC","1 A 120 V AC või 1 A 24 V DC"]
["Torustiku diameeter","mm","","100","150","200","250","250","350"]
["Maht","kW","","1.0","1.0","1.0","2.5","1.5","2.5"]
["Paigaldusavad","","","98 mm x 181 mm keskmed 5 mm Ø avad","98 mm x 181 mm keskmed 5 mm Ø avad","98 mm x 181 mm keskmed 5 mm Ø avad","98 mm x 181 mm keskmed 5 mm Ø avad","98 mm x 181 mm keskmed 5 mm Ø avad","98 mm x 181 mm keskkohad 5 mm _ avad"]
["Maksimaalne ümbris klemmikarbi vahetus läheduses","","","35 °C (töötamise ajal)","35 °C (töötamise ajal)","35 °C (töötamise ajal)","35 °C (töötamise ajal)","35 °C (töötamise ajal)","35 °C (töötamise ajal)"]
["Temperatuurisensor","","","5 koomi temperatuuril 25 °C (tabel 502 1T)","5 koomi temperatuuril 25 °C (tabel 502 1T)","5 koomi temperatuuril 25 °C (tabel 502 1T)","5 koomi temperatuuril 25 °C (tabel 502 1T)","5 koomi temperatuuril 25 °C (tabel 502 1T)","5 koomi temperatuuril 25 °C (tabel 502 1T)"]
["BMSi sättepunkti sisend","","","0–10 V DC","0–10 V DC","0–10 V DC","0–10 V DC","0–10 V DC","0–10 V DC"]
["Temperatuuri juhtimise vahemik","","","0...40 °C / (0–10V 0–100%)","0...40 °C / (0–10V 0–100%)","0...40 °C / (0–10V 0–100%)","0...40 °C / (0–10V 0–100%)","0...40 °C / (0–10V 0–100%)","0...40 °C / (0–10V 0–100%)"]
["Juhtkaitse","","","20 x 5mm 250 mA","20 x 5mm 250 mA","20 x 5mm 250 mA","20 x 5mm 250 mA","20 x 5mm 250 mA","20 x 5mm 250 mA"]
["Power supply","Sagedus","Hz","50/60","50/60","50/60","50/60","50/60","50/60"]
["","Pinge","V","220/250","220/250","220/250","220/250","220/250","220/250"]